## 1. Assumptions
LCoE inputs — hybrid geothermal heating & cooling system
Blue text on yellow = inputs (change these for scenarios). Black text = calculated. Documented sources in column D.
System design
Heating demand peak | 10 | MWth | Challenge brief minimum
Cooling demand peak | 5 | MWth | Challenge brief minimum
Heating FLEH | 2400 | hr/yr | NL DHC typical
Cooling FLEH | 1500 | hr/yr | NL summer cooling demand
Project lifetime | 25 | years | Geothermal industry standard
Discount rate | 7% | fraction | NL geothermal WACC ~7%
Geothermal doublet (BLT-01 producer + USP-01 injector)
Production flow rate | 105 | m³/h | BLT-01 ThermoGIS P50
Production temperature | 77 | °C | BLT-01 ThermoGIS
Injection temperature (after HP-1) | 15 | °C | After return-brine HP
Brine density | 1000 | kg/m³
Brine specific heat | 4180 | J/kg·K
Mass flow rate |  | kg/s | flow / 3600 × density
Direct geothermal heat |  | MWth | Brine 77→35 °C (before HP-1)
Heat pumps
HP-1 COP (return brine 35→15 °C) | 3.5 |  | Typical 70 °C sink
HP-1 heat extracted from brine |  | MW | Brine 35→15 °C
HP-1 electricity input |  | MW | W = Qcold/(COP-1)
HP-1 heat output |  | MWth
HP-2 COP (ATES warm well) | 4 |  | Better source temp
HP-2 heat output | 2.17 | MWth | Sized per design doc
HP-2 electricity input |  | MW
Total heating capacity |  | MWth
Total heating electricity |  | MW
Cooling
Absorption chiller capacity | 3 | MWth | Single-effect LiBr
Absorption chiller COP | 0.7
Electric chiller capacity | 2 | MWth | Peaking unit
Electric chiller COP | 5
ATES cold well capacity | 1 | MWth | Passive cooling
Total cooling capacity |  | MWth

## 2. CapEx
Capital expenditure breakdown
Item | Cost (€M) | % | Source
Subsurface
Drilling USP-01 (1 new well, ~1830 m TVD) | 5 |  | €2.5M base + €1500/m for depth
Workover BLT-01 (recompletion as producer) | 1 |  | NL geothermal benchmark
Reservoir engineering + permitting | 0.5 |  | TNO advisory + EBN approval
Surface plant
Plant building + civil works | 2 |  | Industrial benchmark
Primary heat exchanger (corrosion-resistant) | 1 |  | Duplex SS, brine duty
Heat pump HP-1 (~1 MW electric) | 0.8 |  | Industrial HP, €800/kW
Heat pump HP-2 (~0.5 MW electric) | 0.5 |  | Smaller unit
Absorption chiller (3 MW) | 1 |  | LiBr, €330/kW cooling
Electric chiller (2 MW) | 0.5 |  | Vapor-compression
Pumps, control, BoP | 1 |  | ~5% of plant
ATES system
Warm well + cold well drilling | 1.5 |  | 2 × ~150 m wells, €750k ea.
ATES pumps, HX, heat exchanger | 0.5 |  | Standard ATES skid
Pipelines
Hot brine line BLT-01 → plant (2.0 km) | 2 |  | €1M/km insulated
Cool brine line plant → USP-01 (0.5 km) | 0.3 |  | Less insulation
District network (5 km, primary loop) | 3 |  | €600/m district
Other
Contingency (15%) |  |  | 15% of subtotal
TOTAL CAPEX
CapEx unit metrics
CapEx per MW thermal (combined) |  | €M/MWth

## 3. OpEx
Operating expenditure (annual)
Item | Annual (€k/yr) | % | Basis
Electricity inputs
Heating electricity (HP-1 + HP-2, winter) | 5500 | MWh/yr | See design doc §4
Cooling electricity (EC + auxiliaries) | 1000 | MWh/yr | Summer chiller + pumps
Doublet pump + district circulation | 2250 | MWh/yr | Year-round
Total electricity |  | MWh/yr
NL industrial electricity price | 100 | €/MWh | NL 2024 industrial avg incl. taxes
Electricity annual cost |  | €k/yr
Other operating costs
Maintenance (% of CapEx) | 2.5% |  | NL geothermal benchmark 2-3%
Maintenance cost |  | €k/yr
Labour + monitoring + insurance | 250 | €k/yr | 2 FTE + supervisory + insurance
Reservoir monitoring (chemistry, pressure) | 100 | €k/yr | EBN regulatory requirement
Total annual OpEx
Total OpEx |  | €k/yr

## 4. Energy delivered
Annual energy delivered
Item | Value | Unit | Calculation
Heating delivered |  | MWh/yr | peak heating × FLEH heating
Cooling delivered |  | MWh/yr | peak cooling × FLEH cooling
Total useful energy |  | MWh/yr
Total electricity consumed |  | MWh/yr
System SPF (seasonal performance factor) |  | – | Useful energy / electricity in
CO₂ avoided
Gas emission factor displaced | 0.2 | tCO₂/MWh
NL grid electricity emission factor | 0.25 | tCO₂/MWh | 2026 NL grid average
Gross CO₂ displaced (no gas burned) |  | tCO₂/yr
CO₂ from electricity used |  | tCO₂/yr
Net CO₂ avoided |  | tCO₂/yr

## 5. LCoE
Levelized Cost of Energy (LCoE)
LCoE = (CapEx × CRF + OpEx) / annual energy delivered
Component | Value | Unit
Discount rate (r) |  | –
Lifetime (n) |  | years
Capital recovery factor (CRF) |  | –
Total CapEx |  | €M
Annualized CapEx (CapEx × CRF) |  | €M/yr
Annual OpEx |  | €M/yr
Total annual cost |  | €M/yr
Annual energy delivered |  | MWh/yr
LCoE |  | €/MWh
LCoE in €/kWh |  | €/kWh
Benchmarks (NL onshore geothermal direct use)
EBN/TNO 2020-2024 reported LCoE for NL geothermal: €60-€120/MWh (heat only).
Hybrid systems with heat pumps + cooling typically €80-€140/MWh due to higher CapEx but additional revenue stream.

## 6. Sensitivity
Sensitivity analysis — LCoE swing per ±20% input change
Computed from the shared LCoE model (03_analysis/scripts/lcoe_model.py) — the same model used by the sensitivity tornado notebook and the Monte Carlo. One input is changed at a time from the Assumptions base case (base LCoE ≈ €122/MWh).
Input | Base value | Low (-20%) | High (+20%) | ΔLCoE (low) | ΔLCoE (high)
Drilling cost (€M/well) | 5 | 4 | 6 | -€4.0/MWh | +€4.0/MWh
NL electricity price (€/MWh) | 100 | 80 | 120 | -€5.6/MWh | +€5.6/MWh
Discount rate | 0.07 | 0.056 | 0.084 | -€7.9/MWh | +€8.3/MWh
Heating FLEH (hr/yr) | 2400 | 1920 | 2880 | +€19.6/MWh | -€14.4/MWh
HP-1 COP | 3.5 | 2.8 | 4.2 | +€1.9/MWh | -€1.2/MWh
Project lifetime (years) | 25 | 20 | 30 | +€6.5/MWh | -€3.9/MWh
USP-01 production (% of P50) | 1 | 0.8 | 1.2 | +€2.4/MWh | -€0.5/MWh
Biggest sensitivity by far is heating utilisation (FLEH), then the financing-side levers (discount rate, project lifetime). Doublet flow rate and HP-1 COP are minor LCoE levers within ±20% because the heat pumps efficiently absorb a geothermal shortfall while pumping electricity falls; the material USP-01 risk is the discontinuous case (missing peak demand / needing a second doublet), not a ±20% LCoE gradient.